# CBAS Active Chilled Beams

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 8214 – Chilled Beams

## GENERAL

### SECTION INCLUDES

#### Active chilled beams

### RELATED SECTIONS

#### Division Section 01 – “General Requirements”

#### Division Section 01 – “Special Procedures”

#### Division Section 23 – “Instrumentation and Control Devices for HVAC:  Thermostats, control components and actuators.”

#### Division Section 23 – “Direct Digital Control System for HVAC.”

#### Division Section 23 – “Sequence of Operations for HVAC Controls.”

#### Division Section 23 – “Hydronic Piping:  Connections to heating and cooling coils.”

#### Division Section 23 – “Hydronic Specialties:  Connections to heating and cooling coils.”

#### Division Section 23 – “HVAC Ducts and Casings.”

#### Division Section 23 – “Air Duct Accessories.”

#### Division Section 23 – “Air Outlets and Inlets.”

#### Division Section 26 – “Equipment Wiring:  Electrical characteristics and wiring connections.”

### REFERENCE STANDARDS

#### The following documents form part of the Specifications. Where applicable, local and national codes take preference over the Standards:

##### AHRI 410 – Standard for Forced Circulation Air Cooling and Air Heating Coils.

##### ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy

##### AHRI 880 – Performance Rating of Air Terminals.

##### AHRI 885 – Procedure for Estimating Occupied Space Sound Levels in the Application of Air Terminals and Air Outlets.

##### ASHRAE 62.1 – Ventilation for Acceptable Indoor Air Quality.

##### ASHRAE 200 – Methods of Testing Chilled Beams.

##### ASTM C1071 – Standard Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material).

##### ASTM C1338 Standard Test Method for Determining Fungi Resistance of Insulation Materials and Facings.

##### ASTM E84 – Standard Test Method for Surface Burning Characteristics of Building Materials.

##### ASTM E488/E488M – Standard Test Methods for Strength of Anchors in Concrete Elements.

##### CSA C22.2 No. 236 – Heating and Cooling Equipment.

##### NFPA 70 – National Electrical Code.

##### NFPA 90A – Standard for the Installation of Air Conditioning and Ventilating Systems; National Fire Protection Association.

##### UL 94 – Tests for Flammability of Plastic Materials for Parts in Devices and Appliances.

##### UL 181 – Standard for Factory Made Air Ducts and Air Connectors; Underwriters Laboratories Inc.

##### UL 1995 – Standards for Heating and Cooling Equipment.

### ADMINISTRATION REQUIREMENTS

#### Pre-installation Meeting:  Conduct a pre-installation meeting at least one week prior to the start of the work of this section; require attendance by all affected installers.

### SUBMITTALS

#### Refer to section 01 30 00 – Administrative Requirements for general submittal procedures.

#### Submittals shall include:

##### Product configuration, general assembly drawings and materials used in fabrication.

##### Active beam configuration including:

###### Beam identification per equipment performance schedule

###### Beam length, width and height

###### Beam nozzle type/size

###### Beam coil type (2 or 4 pipe)

##### Performance ratings that relate air and water flow, static pressures, octave band discharge and radiated sound power levels (and/or NC levels, as required).

##### Unit weights.

##### Manufacturer's installation instructions indicating support and hanging instructions and other pertinent connection, installation and start up recommendations.

##### References clearly showing the location of units according to plans and schedules.

##### Operation and maintenance manuals which incorporate operating instructions (including field reset of primary airflow rates), maintenance, repair procedures and parts lists.

### QUALITY ASSURANCE

#### Performance ratings:

##### Active Chilled Beams shall be tested in accordance with ASHRAE Standard 200 - Methods of Testing Chilled Beams.

##### Submitted NC levels shall be based upon standard attenuation values found in AHRI 885 Appendix E unless specifically stated otherwise.

##### Submitted cooling/heating capacities shall include primary airflow rate and temperature as well as supply water flow rate(s) and temperature(s).

### WARRANTY

#### Refer to Section 01 78 00 – Closeout Submittals, for additional warranty requirements.

#### Provide a 12-month manufacturer limited warranty from the date of shipment.

### DELIVERY, STORAGE AND HANDLING

#### Deliver materials to site in manufacturer’s original, unopened containers. Packaging shall be clearly marked with labels indicating manufacturer, products included and location of installation.

## PRODUCTS

### ACCEPTABLE MANUFACTURERS

#### Basis of Design: Titus (Division of Air System Components).

### ACTIVE CHILLED BEAMS

#### Furnish and install Titus model CBAS under sill active chilled beams in the sizes, configurations and capacities indicated on the project schedules and plans.

#### Unit shall comprise a primary air connection, a pressurized inlet plenum feeding a series of room air induction nozzles and an associated heat transfer coil contained in a single unit housing.

#### Unit casing:

##### The unit casing shall be constructed from a minimum 22-gauge galvanized sheet steel.

##### Units shall have a maximum casing height of 25⅛”.

#### Primary air inlet:

##### Manufacturer shall provide a single round or oval side mounted inlet collar of diameter(s) as indicated on the project plans and schedules and suitable for connection to common flexible or rigid ductwork sizes.

##### The inlet collar shall be roll-formed to facilitate the connection of flexible or rigid ductwork.

#### Nozzles shall be of a fixed size, selected with respect to cooling and heating requirements, and constructed of formed sheet metal.

#### Primary air plenum pressure tap:

##### A plenum air pressure tap shall be mounted within the pressurized plenum for measuring the pressure differential between the primary air plenum and the room. The pressure tap manometer connection port shall be fitted to the end of a plastic tube accessible from the side of the unit.

##### Airflow calibration charts that relate the pressure differential reading with the primary airflow rates, shall be furnished with the IOM’s.

#### Mounting brackets:

##### Factory installed mounting brackets shall incorporate slotted holes and designed for wall mounting.

#### Hydronic heat transfer coil:

##### Integral heat transfer coils shall be provided with connections for either 2 or 4 pipe water connections as indicated on plans and schedules. Four pipe configurations shall require separate supply and return connections for chilled and hot water. The coil shall be mounted horizontally and shall be manufactured with seamless copper tubing (½” or ¾” inch outside diameter as indicated on the plans and schedules) with minimum .016 inch wall thickness mechanically fixed to aluminum fins. The aluminum fins shall be limited to no more than ten (10) fins per inch. The coil shall have a working pressure of at least 360 PSI, and be factory tested for leakage at a minimum pressure of 500 PSI.

##### Each chilled beam shall be provided with factory integrated manual air vents. (OPTIONAL, coil shall be provided with factory integrated drain fittings.)

##### Unless otherwise specified, coil connections shall be bare copper for field sweating to the water supply circuit(s). (OPTIONAL, the chilled water coil shall be provided with NPT male threaded fittings. These fittings must be suitable for field connection to a similar NPT female flexible hose spigot and shall be at least 1½” long to facilitate field connection (by others).

##### The coil shall be rated and certified in accordance with AHRI Standard 410.

#### Packaging:

##### Beams shall be delivered to site clean with hydronic coils flushed and fitted with protective caps.

##### Units shall be shipped to site in cartons and labeled with identification tagging.

#### The manufacturer shall provide the following accessories:

##### (OPTIONAL) Lint screens:

###### Manufacturer shall provide zinc plated steel mesh lint screens with galvanized frames fitted to the heat exchange coils. Lint screens shall be removable without the use of tools.

##### (OPTIONAL) Water connection hoses:

###### Manufacturer shall provide ½” or ¾” dia. x (12 inch), (18 inch) or (24 inch) long stainless-steel braided hoses with female swivel connections.

###### Hoses shall be constructed with a KEVLAR® reinforced EPDM core with stainless steel ferrules.

###### Hoses shall be tested for working pressures up to 400 PSIG (at max. operating temperature of 248°F) with a burst pressure of 1600 PSIG.

##### (OPTIONAL) Airflow regulators:

#### Manufacturer shall supply UL94 V-0 rated ABS polymer and UL2043 listed constant volume regulators (CVR’s). CVR’s shall be designed to fit inside rigid round ductwork and located at a minimum distance of three duct diameters upstream of the active chilled beam primary air inlet.

#### Controls:

##### Refer to Section 23 09 13 – Instrumentation and Control Devices for HVAC.

#### Controls Sequence:

##### Refer to Section 23 09 93 – Sequence of Operations for HVAC Controls for controls sequence requirements.

## EXECUTION

### EXAMINATION

#### Verify site conditions are suitable for the installation of terminal units. Verify that the manufacturer’s recommended maintenance and airflow clearances will be obtained before proceeding with the installation. Notify the engineer of any conditions that may affect the operation of the terminal units.

### INSTALLATION

#### Install active beams in locations as indicated on the contract drawings.

#### Install and commission active beams in accordance with the manufacturer’s Installation, Operation and Maintenance manuals.

#### Installation hardware shall be in accordance with the manufacturer’s recommendations and any local codes that dictate installation requirements.

#### Air connections to the main primary air duct shall be made with flexible duct with all joints sealed and made airtight.

#### Before connecting the supply water system(s) to the beams, contractor shall flush the piping system(s) to assure that all debris and other matter have been removed.

#### Contractor shall perform connection of beams to the water circuit(s) by method specified (hard connection using sweated connection or connection using flexible hoses).

#### Balance the primary air to each active chilled beam:

##### Comply with Division 23 Section "Testing, Adjusting, and Balancing for HVAC".  Note that a flow hood cannot be used to measure airflow on active chilled beams since the hood disrupts induction and the normal operation of chilled beam airflow. Instead, airflow to each chilled beam shall be determined by measuring the plenum to room air pressure differential using the factory fitted primary air plenum pressure tap (section H) and converting to airflow by using the airflow calibration charts furnished with the IOM’s.