# CBPE Passive Chilled Beams

Division 23 – Heating, Ventilating, and Air Conditioning

Section 23 8214 – Chilled Beams

## GENERAL

### SECTION INCLUDES

#### Passive chilled beams

### RELATED SECTIONS

#### Division Section 01 – “General Requirements”

#### Division Section 01 – “Special Procedures”

#### Division Section 23 – “Instrumentation and Control Devices for HVAC:  Thermostats, control components and actuators.”

#### Division Section 23 – “Direct Digital Control System for HVAC.”

#### Division Section 23 – “Sequence of Operations for HVAC Controls.”

#### Division Section 23 – “Hydronic Piping:  Connections to heating and cooling coils.”

#### Division Section 23 – “Hydronic Specialties:  Connections to heating and cooling coils.”

#### Division Section 23 – “HVAC Ducts and Casings.”

#### Division Section 23 – “Air Duct Accessories.”

#### Division Section 23 – “Air Outlets and Inlets.”

#### Division Section 26 – “Equipment Wiring:  Electrical characteristics and wiring connections.”

### REFERENCE STANDARDS

#### The following documents form part of the Specifications. Where applicable, local and national codes take preference over the Standards:

##### AHRI 410 – Standard for Forced Circulation Air Cooling and Air Heating Coils.

##### ASHRAE Standard 55 – Thermal Environmental Conditions for Human Occupancy

##### ASHRAE 62.1 – Ventilation for Acceptable Indoor Air Quality.

##### ASHRAE 200 – Methods of Testing Chilled Beams.

##### ASTM C1071 – Standard Specification for Fibrous Glass Duct Lining Insulation (Thermal and Sound Absorbing Material).

##### ASTM C1338 Standard Test Method for Determining Fungi Resistance of Insulation Materials and Facings.

##### ASTM E84 – Standard Test Method for Surface Burning Characteristics of Building Materials.

##### ASTM E488/E488M – Standard Test Methods for Strength of Anchors in Concrete Elements.

##### CSA C22.2 No. 236 – Heating and Cooling Equipment.

##### NFPA 70 – National Electrical Code.

##### NFPA 90A – Standard for the Installation of Air Conditioning and Ventilating Systems; National Fire Protection Association.

##### UL 94 – Tests for Flammability of Plastic Materials for Parts in Devices and Appliances.

##### UL 181 – Standard for Factory Made Air Ducts and Air Connectors; Underwriters Laboratories Inc.

##### UL 1995 – Standards for Heating and Cooling Equipment.

### ADMINISTRATION REQUIREMENTS

#### Pre-installation Meeting:  Conduct a pre-installation meeting at least one week prior to the start of the work of this section; require attendance by all affected installers.

### SUBMITTALS

#### Refer to section 01 30 00 – Administrative Requirements for general submittal procedures.

#### Submittals shall include:

##### Product configuration, general assembly drawings and materials used in fabrication.

##### Passive beam configuration including:

###### Beam identification per equipment performance schedule

###### Beam length, width and height

##### Performance ratings that relate water flow, water temperatures and cooling capacities.

##### Unit weights.

##### Manufacturer's installation instructions indicating support and hanging instructions and other pertinent connection, installation and start up recommendations.

##### References clearly showing the location of units according to plans and schedules.

##### Operation and maintenance manuals which incorporate operating instructions, maintenance, repair procedures and parts lists.

### QUALITY ASSURANCE

#### Performance ratings:

##### Passive Chilled Beams shall be tested in accordance with ASHRAE Standard 200 - Methods of Testing Chilled Beams.

##### Submitted cooling capacities shall include supply water flow rate(s) and temperature(s).

### WARRANTY

#### Refer to Section 01 78 00 – Closeout Submittals, for additional warranty requirements.

#### Provide a 12-month manufacturer limited warranty from the date of shipment.

### DELIVERY, STORAGE AND HANDLING

#### Deliver materials to site in manufacturer’s original, unopened containers. Packaging shall be clearly marked with labels indicating manufacturer, products included and location of installation.

## PRODUCTS

### ACCEPTABLE MANUFACTURERS

#### Basis of Design: Titus (Division of Air System Components).

### PASSIVE CHILLED BEAMS

#### Furnish and install Titus model CBPE exposed passive chilled beams in the sizes, configurations and capacities indicated on the project schedules and plans.

#### Unit shall comprise a sensible cooling coil housed in an architectural casing designed for use with or without (exposed mount) a suspended ceiling.

#### Unit casing:

##### The unit casing shall be constructed from a minimum 22-gauge galvanized sheet steel.

##### Units shall have a maximum casing height of 10⅞”.

#### Face:

##### The face of the beam shall consist of a perforated section of 50% free area.

##### The perforated face shall be sectioned into two pieces so either section can be moved to the opposing side for coil cleaning. The entire visible face sections and all visible surfaces shall be finished in white powder coat paint or (OPTIONAL) as specified by the architect.

#### Mounting brackets:

##### Mounting brackets shall be factory installed along the length of the unit and incorporate slotted holes for hanging using threaded rods.

#### Sensible cooling coil:

##### Sensible cooling coils shall be provided with connections for 2-pipe water connections. The coil shall be mounted horizontally and shall be manufactured with seamless copper tubing ½” outside diameter with minimum .016 inch wall thickness mechanically fixed to aluminum fins. The aluminum fins shall be limited to no more than six (6) fins per inch. The coil shall have a working pressure of at least 360 PSI, and be factory tested for leakage at a minimum pressure of 500 PSI.

##### Each chilled beam shall be provided with factory integrated manual air vents. (OPTIONAL, coil shall be provided with factory integrated drain fittings.)

##### Unless otherwise specified, coil connections shall be bare copper for field sweating to the water supply circuit. (OPTIONAL, the chilled water coil shall be provided with NPT male threaded fittings. These fittings must be suitable for field connection to a similar NPT female flexible hose spigot and shall be at least 1½” long to facilitate field connection (by others).

##### The coil shall be rated and certified in accordance with AHRI Standard 410.

#### Packaging:

##### Beams shall be delivered to site clean with hydronic coils flushed and fitted with protective caps.

##### Units shall be shipped to site in cartons and labeled with identification tagging.

#### Controls:

##### Refer to Section 23 09 13 – Instrumentation and Control Devices for HVAC.

#### Controls Sequence:

##### Refer to Section 23 09 93 – Sequence of Operations for HVAC Controls for controls sequence requirements.

## EXECUTION

### EXAMINATION

#### Verify site conditions are suitable for the installation of terminal units. Verify that the manufacturer’s recommended maintenance and airflow clearances will be obtained before proceeding with the installation. Notify the engineer of any conditions that may affect the operation of the terminal units.

### INSTALLATION

#### Install passive beams in locations as indicated on the contract drawings.

#### Install and commission passive beams in accordance with the manufacturer’s Installation, Operation and Maintenance manuals.

#### Installation hardware shall be in accordance with the manufacturer’s recommendations and any local codes that dictate hanging requirements.

#### Passive chilled beams up to six feet in length shall be independently suspended from the structure above by four (4) threaded rods of ⅜” diameter (provided by the installing contractor).  For beams beyond six feet in length, a minimum of six (6) threaded rods of ⅜” diameter shall be used. The upper end of the rods shall be suspended from strut channels that are a) mounted perpendicular to the beam length and b) at least four inches wider than the beam to facilitate relocation of the threaded rods along their length. The beam shall then be positioned above the acoustical ceiling grid and lowered into the grid module by adjusting the nuts connecting the threaded rods to the beam.

#### Before connecting the supply water system(s) to the beams, contractor shall flush the piping system(s) to assure that all debris and other matter have been removed.

#### Contractor shall perform connection of beams to the water circuit(s) by method specified (hard connection using sweated connection or connection using flexible hoses).